Weave Radiant Textile Panels

- Manufacturer: Lindner PARC

- Manufacturer Contact: ceilings@Lindner-Group.com

- Product: Weave

- Radiant heating and cooling shall be provided by Weave Radiant Textile Panels, consisting of single elements for ceiling

      - Description:

        - The contractor shall furnish and install Weave Radiant Textile Panels per the reflected ceiling plan (RCP)

        - Panels shall be made to measure in any size from 300 x 600mm to 1500 x 3000mm [11.8 inch x 23.6 inch to 59.1 inch to 118.1 inch]

      - The radiant ceiling panels shall have the following construction:

    - Perforated aluminium radiant panel with minimum 33% perforation

    - High torsional strength extruded aluminium frame

    - The panel shall include a glass mineral insulation layer

    - All visible surfaces shall be wrapped in aluminised Kvadrat Casa Vero textile, with textile grain direction coordinated to match for all adjacent panels

    - Textile shall be applied to the radiant panel using springs for tensioning

      - The radiant panel performance shall be:

- Minimum Class B acoustic performance, tested to ISO 11654

- Minimum 79.5 Watts per square meter heating performance (referring to active panel area as per DIN EN 14037), at 15 Kelvin Delta T (Mean Water Temperature – Room Air Temperature). Tested to DIN EN 14037 at an accredited, independent facility

- Minimum 82 Watts per square meter cooling performance (referring to active panel area as per DIN EN 14240), at 10 Kelvin Delta T (Room Air Temperature – Mean Water Temperature). Tested to DIN EN 14240

      - The radiant ceiling panel finish shall be (select one):

- Kvadrat Casa Vero 1122

- Kvadrat Casa Vero 1100

- Kvadrat Casa Vero 1250

- Kvadrat Casa Vero 1212

      - The radiant panel shall be provided with the following mounting accessories:

- Torsion springs

- Access cables

      - The manufacturer shall provide the following accessories (select all that apply):

- Push-fit braided flex hoses for panel-to-panel connections

- Core mounting system, by Lindner PARC, compatible with torsion spring mounting